## Slide 1
Transformer condition assessment with an integrated test van

## Slide 3: Testing and Standards for Power Transformers
CIGRE
  CIGRE Brochure 342 (SFRA-FRAX)
  CIGRE Brochure 414 (DFR-IDAX)
  CIGRE Brochure 445 (Guide for Transformer Maintenance)
IEC, TC 14
  IEC 60076-1, Power Transformers
  IEC 60076-2, Temperature rise
  IEC 60076-3, Insulation levels, dielectric tests and external clearances in air
  IEC 60076-18, Measurement of frequency response (SFRA)
ANSI, IEEE Transformer Committee
  IEEE C57.152 (former IEEE 62-1995)
  IEEE C57.12.00-2006 (under revision)
  IEEE C57.12.90-2006 (under revision)
  IEEE PC57.149 (SFRA)
GOST
  GOST 11677-85, Power Transformers

## Slide 4: Guides and standards for transformer testing
Most standards (IEC and ANSI/IEEE) are focusing on new transformers and factory testing
Workgroups in e.g. Cigré have over the years produced a lot of Technical Brochures (TB) e.g. on sweep frequency response measurements (TB342), partial discharge (TB366), dielectric response measurements (TB414) etc
IEEE 62-1995 “Diagnostic Field Testing of Fluid-Filled Power Transformers, Regulators, and Reactors” is probably the most well-known guide for diagnostic field testing of oil filled power transformers. The guide today belong to the IEEE C57-series and last published revision is C57.152-2013
Notes: 4

## Slide 5: Cigré Technical Brochure 445, 2011 Guide for Transformer Maintenance

## Slide 6: CIGRE TB 445
  Cigré TB 445, ”Guide for Transformer Maintenance”, was published 2011
  TB 445 is a comprehensive combination of education handbook, transformer encyclopedia and a guide for transformer maintenance including guidelines for how to perform measurements in the field
Notes: 6

## Slide 7
From CIGRE TB445 (2011)

## Slide 8: ”Diagnostic” matrix CIGRE TB445
Notes: 8

## Slide 9: Transformer testing by Megger
STANDARD TEST TYPES |  |  | MEGGER TEST SETS |  |  |  |  |  |  |  |  |  |  | 
Component |  | Test | Delta | IDAX | MIT | FRAX | MLR | TTR | MTO | LTC 135 | MoM | TRAX | OTS | KF
Windings |  | Resistance |  |  |  |  |  |  | X | X |  | X |  | 
 |  | Ratio/polarity |  |  |  |  |  | X |  |  |  | X |  | 
 |  | Excitation current | X | X |  |  |  | X |  |  |  | X |  | 
 |  | Short-circuit impedance |  |  |  | X | X |  |  |  |  | X |  | 
 |  | Frequency response analysis |  |  |  | X |  |  |  |  |  |  |  | 
 |  | Insulation resistance |  |  | X |  |  |  |  |  |  |  |  | 
 |  | Capacitance | X | X |  |  |  |  |  |  |  | X |  | 
 |  | Power factor/tan delta | X | X |  |  |  |  |  |  |  | X |  | 
 |  | Dielectric frequency response |  | X |  |  |  |  |  |  |  |  |  | 
Bushings |  | Capacitance | X | X |  |  |  |  |  |  |  | X |  | 
 |  | Power factor/tan delta | X | X |  |  |  |  |  |  |  | X |  | 
 |  | Dielectric frequency response |  | X |  |  |  |  |  |  |  |  |  | 
Insulating oil |  | Water content |  |  |  |  |  |  |  |  |  |  |  | X
 |  | Dielectric strength |  |  |  |  |  |  |  |  |  |  | X | 
 |  | Power factor/tan delta | X | X |  |  |  |  |  |  |  | X |  | 
Cellulose insulation |  | Moisture content |  | X |  |  |  |  |  |  |  |  |  | 
Tap changers | Load | Resistance |  |  |  |  |  |  | X | X |  | X |  | 
 |  | Ratio |  |  |  |  |  | X |  |  |  | X |  | 
 |  | Continuity (make before break) |  |  |  |  |  |  | X | X |  | X |  | 
 |  | Dynamic resistance (DRM) |  |  |  |  |  |  |  | X |  | X |  | 
 | De-energized | Resistance |  |  |  |  |  |  | X | X |  | X |  | 
 |  | Ratio |  |  |  |  |  | X |  |  |  | X |  | 
Core/Tank |  | Insulation resistance |  | X | X |  |  |  |  |  |  |  |  | 
 |  | Frequency response analysis |  |  |  | X |  |  |  |  |  |  |  | 
 |  | Ground test |  |  |  |  |  |  |  |  | X | X |  | 

## Slide 10: So many tests to do?

## Slide 11: Ambient conditions?
Or tangled cables?

## Slide 12: Number of climbs up and down a ladder?

## Slide 14
The Variant: cable fault location, cable testing and diagnosis in a modular system
Cable test van

## Slide 15: Historie Kabelmesswagen
First cable test van
1969
1980
500 test vans delivered to USSR
1985
1000 vans to USSR
1988
2000 vans worldwide
2012
4000 vans worldwide
1997
Vario KMT
2006
Centrix 1/3-ph
Variant
1995
Hitec 2000
History of cable test vans (SebaKMT)

## Slide 16
History of transformer test vans

## Slide 17
Operators view (inside)
Touch screen
Power supply, control and safety unit
19” cabinet drawers with test instruments inside
Keyboard and mouse (exten-sible table)

## Slide 18
View from rear of van (“doors open”)
Drums w. 30 m cables for HV tests (IR, tanD /Capacitance)
Drums w. mains supply cable
Protective earthing cable
Drums 30 m cables for winding resistance / TTR tests (3ph + neutral, HV and LV side)
Safety / alarm system and cables
HV-LV Switch for measuring circuits

## Slide 19
Concept for small vehicles:

## Slide 20: HV commutator
tanD/C test
(Delta 4110) 10kV AC
Insulation
Resistance
(S 1 -1068) 10kV DC
HV cable, 30m
Measure «Blue», 30m
Measure «red», 30m
Interlock, 30m
DFR/ Moisture
(IDAX 300 +VAX 2kV)

## Slide 21: LV commutator
Winding
resistance
(MTO300)
Turns ratio/
Phase
(TTR300)
H multicable, A-B-C-N, 30m
X multicable, a-b-c-n, 30m

## Slide 22: External design

## Slide 23
Designation
Commissioning
Preventive maintenance
Outage troubleshooting
After repair check
Issues that can be identified:
deterioration of electrical insulation
mechanical displacements/damage
winding-, bushing-, tap changer-, core- and oil condition
check for ratio, vector group, no-load& load losses

## Slide 24
Unique features
Routine and advanced diagnostic tests
Centralized control and reporting
Two sets of cable (HV & LV) shared among instruments
Automated test circuit arrangement and switching process
Safe operation and user guidance through the tests

## Slide 25
Routine and diagnostic tests onboard:
Insulation Resistance
DC Winding resistance / Tap Changer Test
Capacitance and dissipation factor for transformer and bushings
Turn ratio and vector group verification
Moisture-in-cellulose assessment with DFR technique
Short circuit impedance (optional)
Power losses for no-load and short circuit conditions (optional)
Frequency Response Analysis (optional)
Withstand tests at elevated voltage up to 100 kV AC 50 Hz and 70 kV DC (optional)
Oil breakdown test (optional)

## Slide 26: Optional: HV source on board
Single phase HV source
100 kV AC 50 Hz
70 kV DC

## Slide 27: Optional: power loss measurement at reduced voltage
Loss measurement at reduced voltage of 380 / 230 V is a good compromise under on site conditions (due to limitations in power and voltage sources)
No-load circuit
Short circuit condition
Important to have a factory data on losses at reduced voltage as reference!

## Slide 28
Well-known components:

## Slide 29
Specification:

## Slide 30
Software: Device selector

## Slide 31: Optional: power loss measurement at reduced voltage
Important to have a factory data on losses at reduced voltage as reference!

## Slide 32
Software: PowerDB

## Slide 33
Complete report with PowerDB

## Slide 35: Conclusions
Transformer test van concept:
  combines routine electric tests and advanced diagnostic techniques
  allows a complete transformer check in field.
Field experiences:
  substantial testing time saving >70%
  help prevent accidents
Streamlined data handling:
  reporting, database for assessing results, comparing w previous tests and eventually establishing trend of the transformer condition

## Slide 36
Thank you!